## annexe
TECHNICAL DATA SHEET / ANNEXE TECH. : ASP
Axially Split Case Pump / pompes axiales à plan de joint | [6 empty] | P
красным - поля, обязательные для заполнения
Запрос |  | Тех. Бюро | КЕЛЬВИН
Devis/Anfrage |  | Vertriebsbüro
Заказ | V | Ответственное лицо | Кудинова; Гавриков
Commande/Auftrag |  | resp. dossier / Bearbeiter
проект
Projet / Projekt
A . Рабочие условия / Conditions de fonctionnement / Produktdaten
Тип установки | Heating and air conditionning systems |  |  | Температура | 70 |  |  | °C
Type d'installation / Anlage |  |  |  | Température/Temp.
Жидкость | Heating Water / Eau chauffage |  |  | вязкость |  |  |  | 10-6m2/s
Fluide/Anwendung |  |  |  | Viscosité ( cSt )
Примеси и % примесей | 0 |  |  | плотность |  |  |  | kg/m3
Additifs/Chem.Zusätze |  |  |  | Densité kg / m3
примечания | . |  |  | PH
Rem/Bemerkungen
B . Рабочие параметры / caractéristiques hydrauliques / Betriebsdaten
Подача одного насоса | 1500 | m3/h |  | Давление на входе |  | 3.92 |  | bar, манометрическое
Débit / Förderstrom | 416.6667 | l/s |  | Pression à l'aspt /Zulaufdruck
Напор одного насоса | 65 | mcl (метры) |  | Максимальное допустимое давление на выходе |  | 15.69 |  | bar, манометрическое
hauteur manometrique totale / Förderhöhe |  |  |  | Pression maxi de fonctionnement
NPSH имеющийся |  | m
disponible / verfügbar
C . Комплектация насоса /Descriptif fourniture/Pumpendaten
Количество насосов | 1 | насосная часть |  | Suction Flange | PN16 |  |  | Flat
Quantité/ Anzahl |  | Pompe arbre nu / Nur die Pumpe (ohne Motor etc. ) |  | Bride a l aspiration
|  | насос на раме без мотора |  | Delivery Flange | PN16 |  |  | Flat
|  | Groupe sans moteur / Pumpe mit Grundplatte und Kupplung, ohne Motor |  | Bride au refoulement
|  | насос на раме с мотором | X | According to standard | ISO 7005-1-2
|  | Groupe complet / Pumpe komplett mit Motor |  | Conforme norme
направление вращения
Конструкция насоса
Options Pompe / Optionen
сальниковая набивка
Tresse / Stopfbuchspackung
X
торцевое уплотнение
GM / Gleitringdichtung
диаметр рабочего колеса |  | mm
diam. de roue/Laufraddurchmesser only, when selected by customer
дополнительные опции | отметить если есть требования к материалу насоса и материалу рабочего колеса
Options speciale / Optionen
Мотор/ Moteur / motoren |  |  | Мотор для работы с частотным преобразователем/Motor use with frequency converter |  |  |  |  | нет
Мощность / P / Motorleistung | 355 | kW | число полюсов / N polig
напряжение и частота | 3 ~ Δ 400 V 50Hz |  | скорость вращения / vitesse de rotation |  |  |  |  | rpm
класс защиты / Schutzart | *
тепловая защита
дополнительные опции мотора | отметить если есть специальные требования к мотору
Options moteur / Optionen
D . Сертификат / certificat / zertifikat
требуемые сертификаты / liste : | nothing / aucun /
E . Предложение (заполняется продавцом) | No. |  |  | Delivery time |  |  |  | недель (DDP Москва)
N° Devis / Angebot |  |  |  | Délai / Lieferzeit |  |  |  | (except holidays)
Тип насоса |  | SCP 350/470НА-355/4-Т4-С1/E1
Type de pompe / Typ
Article N° / Art.-Nr. |  |  |  | примечания / Rem. / Bemerkungen
annexe 4104001 ASP 2006-06 ed07
MOE (for one unit) |  | X |  | Delivery time
OTP (for one unit) |  |  |  | Indicative Delivery Time
TPL (for one unit)
Salmson Batiment collectif | [6 empty] | Standard CW
Salmson cycle de l'eau | [6 empty] | Opposit CCW
Salmson international
Salmson Habitat individuel
Salmson Industrie
Wilo Chine
Wilo Russie
Wilo Lituanie
Wilo Grèce
Wilo
.
.
Wilo
1
2
3
4
5
* |  |  |  | *
No communicated / non communiqué |  |  |  | No communicated / non communiqué
Water Supply / Adduction |  |  |  | Clear Water / eau claire
Booster / Surpression |  |  |  | River Water / eau de riviere
Drink Water / eau potable |  |  |  | Sea water / eau de mer
Fire protection / protection incendie |  |  |  | Heating Water / Eau chauffage
Sprinkling / Sprinkler |  |  |  | Cold Water / Eau glacée
Heating and air conditionning systems |  |  |  | Cooling water / eau de refroidissement
Hot Water / eau chaude |  |  |  | Water with additive / Eau traitée
Pumping, transfer sea water |  |  |  | Industrial fluid / fluide industriel
Pumping, transfer industrial fluids |  |  |  | Other / autre
Irrigation
standard |  | IP 65 |  | *
WEG |  | IP 55 |  | Flat
ABB |  | IP 54 |  | Flat raised
VEM |  | IP 44 |  | Grooved (DEF)
SIEMENS |  | IP 23 |  | 125
(other/autre/andere) |  | * |  | 250
Diesel engine |  | 2 |  | NFEN 1092-1-2 DIN 2501 (PN16)
Diesel engine IVECO |  | 4 |  | NFEN 1092-1-2
|  | 6 |  | ISO 7005-1-2
Spécial |  | 8 |  | ASA
Customer / client |  | * |  | ANSI
*
|  | CTP / KLF |  | PN10
|  | no |  | PN16
|  | * |  | PN20
PN25
PN40
*
ANSI
3 ~ 230-400 V 50Hz |  | 0.75
3 ~ Δ 400 V 50Hz |  | 1.1
. |  | 1.5
3 ~ 240-415 V 50Hz |  | 2.2
3 ~ 254-440 V 50Hz |  | 3
3 ~ 288-500 V 50Hz |  | 4
. |  | 5.5
3 ~ Δ 415 V 50Hz |  | 7.5
3 ~ Δ 500 V 50Hz |  | 11
. |  | 15
3 ~ 220-380 V 60Hz |  | 18.5
3 ~ 254-440 V 60Hz |  | 22
3 ~ 265-460 V 60Hz |  | 30
3 ~ 277-480 V 60Hz |  | 37
3 ~ 332-575 V 60Hz |  | 45
3 ~ Δ 208 V 60Hz |  | 55
3 ~ Δ 380 V 60Hz |  | 75
3 ~ Δ 440 V 60Hz |  | 90
3 ~ Δ 460 V 60Hz |  | 110
. |  | 132
1 ~ 110 V 50Hz |  | 160
1 ~ 230 V 50Hz |  | 185
1 ~ 240 V 50Hz |  | 200
1 ~ 110 V 60Hz |  | 250
300
315
3 ~ Δ 3300 V 50Hz |  | 355
3 ~ Δ 5500 V 50Hz |  | 400
3 ~ Δ 6000 V 50Hz |  | 450
3 ~ Δ 6600 V 50Hz |  | 500
3 ~ Δ 10000 V 50Hz |  | 560
630
thermique/thermic |  | 710
Autre/other |  | 750
800
900
1000
OTP (for one unit) |  | 1120
PRU (for one unit)
Std unbalanced : Carbone / ceramic / EPDM /-8°c to 120°c |  |  |  | nothing / aucun /
Std balanced : Carbone / ceramic / EPDM /-8°c to 120°c |  |  |  | CE safty certificat
Certificat of Quality and Quantity by manufacture
Std unbalanced : Carbone/ Carbure SIC / EPDM |  |  |  | Certificat of origin
Std balanced : Carbone/ Carbure SIC / EPDM |  |  |  | certificat of conformity (2.1 EN 10204)
certificat of conformity (2.2 EN 10204)
Std unbalanced : Carbone/ Carbure SIC / VITON |  |  |  | certificat of control (3.1B EN 10204)
Std balanced : Carbone/ Carbure SIC / VITON |  |  |  | certificat of pressure test (EN 12162)
certificat of conformity material (2.2 EN 10204)
Burgmann MG1 G60 : Carbone / ceramic / EPDM |  |  |  | material attestation
Burgmann balanced : Carbone / ceramic / EPDM |  |  |  | CE safty certificat (Motor)
Certificat of conformity (Motor)(2.1 EN 10204)
Burgmann MG1 G60 : Carbone/ Carbure SIC / EPDM |  |  |  | certificat of conformity (Motor)(2.2 EN 10204)
Burgmann balanced : Carbone/ Carbure SIC / EPDM |  |  |  | certificat of control (Motor)(3.1B EN 10204)
Burgmann MG1 G60 : Carbone/ Carbure SIC / VITON
Burgmann balanced : Carbone/ Carbure SIC / VITON
Special
Construction 1 Casing/Corps : Cast iron / Fte FGL / BS1452 Gr 260 Wear ring/Bague d'usure : Bronze BS1400 LB2 / G-CuPb 15 Sn / DIN 1705 Impeller/Roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Imp. nut/ecrou roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Shaft/Arbre : Stainless steel BS970 410 S21 / X12 Cr13 All fasteners,pipe .../ fixt , tube : Carbon steel, Copper , Brass | [9 empty] | Construction 1 Casing/Corps : Cast iron / Fte FGL / BS1452 Gr 260 Wear ring/Bague d'usure : Bronze BS1400 LB2 / G-CuPb 15 Sn / DIN 1705 Impeller/Roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Imp. nut/ecrou roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Shaft/Arbre : Stainless steel BS970 410 S21 / X12 Cr13 All fasteners,pipe .../ fixt , tube : Carbon steel, Copper , Brass
Construction 2 Casing/Corps : Cast Iron / 0.6660 / GGL-NiCr20 2 (Ni resist 2) / BS3468:L-NiCr20 2 Wear ring/Bague d'usure : Bronze zinc free BS1400 CT1 - G Cu Sn10 - DIN 1705 Impeller/Roue : Bronze zinc free BS1400 CT1 - G Cu Sn10 - DIN 1705 Imp. nut/ecrou roue : Bronze zinc free BS1400 CT1 - G Cu Sn10 - DIN 1705 Shaft/Arbre : Stainless steel BS970 316 S16 / X5 CrNiMo1810 All fasteners,pipe .../ fixt , tube : Stainless steel | [9 empty] | Construction 2 Casing/Corps : Cast Iron / 0.6660 / GGL-NiCr20 2 (Ni resist 2) / BS3468:L-NiCr20 2 Wear ring/Bague d'usure : Bronze zinc free BS1400 CT1 - G Cu Sn10 - DIN 1705 Impeller/Roue : Bronze zinc free BS1400 CT1 - G Cu Sn10 - DIN 1705 Imp. nut/ecrou roue : Bronze zinc free BS1400 CT1 - G Cu Sn10 - DIN 1705 Shaft/Arbre : Stainless steel BS970 316 S16 / X5 CrNiMo1810 All fasteners,pipe .../ fixt , tube : Stainless steel
Construction 3 Casing/Corps : stainless steel BS3100-316 C16 / G-X6 CrMo1605 Wear ring/Bague d'usure : stainless steel BS3100-316 C16 / G-X6 CrMo1605 Impeller/Roue : stainless steel BS3100-316 C16 / G-X6 CrMo1605 Imp. nut/ecrou roue : stainless steel BS970 316 S16 / X5 CrNiMo1810 Shaft/Arbre : stainless steel BS970 316 S16 / X5 CrNiMo1810 All fasteners,pipe .../ fixt , tube : Stainless steel | [9 empty] | Construction 3 Casing/Corps : stainless steel BS3100-316 C16 / G-X6 CrMo1605 Wear ring/Bague d'usure : stainless steel BS3100-316 C16 / G-X6 CrMo1605 Impeller/Roue : stainless steel BS3100-316 C16 / G-X6 CrMo1605 Imp. nut/ecrou roue : stainless steel BS970 316 S16 / X5 CrNiMo1810 Shaft/Arbre : stainless steel BS970 316 S16 / X5 CrNiMo1810 All fasteners,pipe .../ fixt , tube : Stainless steel
Construction 4 Casing/Corps : Ductile iron / Fte GGG 50 / BS2789 Gr 500 / 0.705 Wear ring/Bague d'usure : Bronze BS1400 LB2 / G-CuPb 15 Sn / DIN 1705 Impeller/Roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Imp. nut/ecrou roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Shaft/Arbre : Stainless steel BS970 410 S21 / X12 Cr13 All fasteners,pipe .../ fixt , tube : Carbon steel, Copper , Brass | [9 empty] | Construction 4 Casing/Corps : Ductile iron / Fte GGG 50 / BS2789 Gr 500 / 0.705 Wear ring/Bague d'usure : Bronze BS1400 LB2 / G-CuPb 15 Sn / DIN 1705 Impeller/Roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Imp. nut/ecrou roue : Bronze BS1400 LG2 / G-CuSn5ZnPb / DIN 1705 Shaft/Arbre : Stainless steel BS970 410 S21 / X12 Cr13 All fasteners,pipe .../ fixt , tube : Carbon steel, Copper , Brass
Special construction /Construction spéciale | [9 empty] | Special construction /Construction spéciale
Gland packing : Graphite impregnated Lantern ring : Bronze / 2.1050.01 / G-CuSn10 / BS1400:CT1 shaft sleeves : Bronze / 2.1096.01 / G-CuSn5 ZnPb / BS1400:LG2 Gland :
Gland packing : Graphite impregnated Lantern ring : Bronze zinc free / 2.1050.01 / G-CuSn10 / BS1400:CT1 shaft sleeves : Bronze zinc free / 2.1050.01 / G-CuSn10 / BS1400:CT1 Gland :
Gland packing : Graphite impregnated Lantern ring : Stainless steel BS970 316 S16 / X5 CrNiMo1810 shaft sleeves : Stainless steel BS970 316 S16 / X5 CrNiMo1810 Gland :
Without shaft sleeve
shaft sleeve : Bronze / 2.1096.01 / G-CuSn5 ZnPb / BS1400:LG2
shaft sleeve : Bronze free zinc / 2.1050.01 / G-CuSn10 / BS1400:CT1
shaft sleeve : Stainless steel BS970 316 S16 / X5 CrNiMo1810
Note on K17: densité 20° 998 30° 995 40° 992 50° 988 60° 983 70° 978 80° 972 90° 965 100° 958 110° 951 120° 943 130° 935 140° 926 150° 917 sea water 1030
Note on K35: Pour PN 16 DN65 4 trous conformement a DIN Et non 8 comme impose ou le permet ISO et NFEN
Please send us all documentation and data from the customer SVP nous transmettre toutes informations et données communiquées par le client
CW
CCW